MODBUSRTU

The system adopts UART half duplex asynchronous serial communication mode, adopts master-slave mode, and the master control board is a slave

I. Transmission format Communication mode: half duplex asynchronous serial communication Baud rate: 2400BPS

Data bit: 8BIT, low bit first parity: none

Start bit: 1BIT (low level)

Stop bit: 1BIT (high level)

ⅡCommunication protocol: MODBUSRTU protocol

2.1 Overview

Master/slave communication: host: upper computer; Slave: main control board. Data transmission format per frame:

| Device address | Function code | Data | CRC check |
| --- | --- | --- | --- |
| 8bits | 8bits | N*8bits | 16bits |

Device address: slave device address, range 1~16 (related to SW2 dialing) Function code: read (0X03) or write (0X06/0X10) function data: read and write communication data in the function.

CRC check:

CRC verification adopts CRC-16/X25X16+X12+X5+1

The check code is used to check all data.

2.2 Function code and data definition

2.2.1 Function code definition

The detailed description of the function code can be seen in the MODBUS protocol. This protocol uses three kinds of function codes. See the following description for details:

Function code=03: Read multiple save registers. The master requests to read multiple 8-bit binary data from the slave. The data structure is defined in the following table:

Host (request)	Slave (answering)

| Device address | Device address |
| --- | --- |
| Function code (03) | Function code (03) |
| Register start address high bit | Data length |
| Register start address low bit bitbiovbbitorder | Data 1 high bit |
| Register number high bit | Data 1 low bit |
| Register number low bit | ... |
| CRC check low bit | ... |
| CRCcheck high bit | Data N high bit |
|  | Data N low bit |
|  | CRC check low bit |
|  | CRC check high bit |

Function code=06H: Preset (write) a single register function, and the master sends two 8-bit binary data to the slave. The data structure is defined in the following table:

Host (request)	Slave (answering)

| Device address | Device address |
| --- | --- |
| Function code (06) | Function code (06) |
| Register start address high bit bitbit | Register start address high bit |
| Register start address low bit bitbitbitbitbitbiovbbitorder | Register start address low bit bitbiovbbitorder |
| Data high bit | Data high bit |
| Data low bit | Data low bit |
| CRC check low bit | CRC check low bit |
| CRC check high bit | CRC check high bit |

Function code=16: Preset (write) multiple registers, and the master sends multiple 8-bit binary data to the slave. The data structure is defined in the following table:

Host (request)	Slave (answering)

| Device address | Device address |
| --- | --- |
| Function code (16) | Function code (16) |
| Register start address high bit | Register start address high bit |
| Register start address low bit | Register start address low bit |
| Register number high bit | Register number high bit |
| Register number low bit | Register number low bit |
| Data length | CRC check low bit |
| Data 1 high bit | CRC check high bit |
| Data 1 low bit |  |
| ... |  |
| ... |  |
| Data N high bit |  |
| Data N low bit |  |
| CRC check low bit |  |
| CRC check high bit |  |

三丶 Communication address

| Address | Function | Content | Word length | Function description | Remark |  |
| --- | --- | --- | --- | --- | --- | --- |
| 2000 | 03/06/16 | System on off switch | Double byte | 0~1 |  |  |
| 2001 | 03/06/16 | System mode | Double byte | 0: Cooling 1: Floor heating; 2: Fan coil heating; 3: Curve heating; 4: Time division heating; 5: Hot water | The adjustable range must be 0~1, because other modes are unstable |  |
| 2002 | 03/06/16 | Cooling setting temperature | Double byte | 10~25 |  |  |
| 2003 | 03/06/16 | Heating setting temperature | Double byte | 20~Controller parameter 17 |  |  |
| 2004 | 03/06/16 | Hot water setting tempereature | Double byte | 20~Controller parameter 17 |  |  |
| 2005 | 03/06/16 | Emergency swithc | Double byte | 0~2 |  | The adjustable range is 0~2. 0 refers to the operation according to the measured value of the emergency switch on the main board, 1 refers to the forced connection of the emergency switch, 2 refers to the forced disconnection of the emergency switch, and the default is 0. |  |
|  |  | switch |  |  |  |  |  |
| 2006 | 03/06/16 | Reserve | Double byte |  |  |  |
| 2007 | 03/06/16 | Reserve | Double byte |  |  |  |
| 2008 | 03/06/16 | Reserve | Double byte |  |  |  |
| 2009 | 03/06/16 | Reserve | Double byte |  |  |  |
| 2010 | 03/06/16 | Controller control parameter 0 heating start return difference | Double byte | 2~18 | 5 |  |
| 2011 | 03/06/16 | Controller control parameter 0 cooling start return difference | Double byte | 2~18 | 5 |  |
| 2012 | 03/06/16 | Wire control paramete2 Water pump working way | Double byte | 0~2 | 2 |  |

| 2013 | 03/06/16 | Wire control parameter 3 Water pump switching interval time | Double byte | 2～20MIN | 5 |
| --- | --- | --- | --- | --- | --- |
| 2014 | 03/06/16 | Wire control parameter 4 Compressor cumulative running time entre deforst | Double byte | 20MIN~90MIN | 45MIN |
| 2015 | 03/06/16 | Wire control parameter 5 Outdoor coil temperature to enter defrost mode | Double byte | -15℃~-1℃ | -3℃ |
| 2016 | 03/06/16 | Wire control parameter 6 Maximum defrost time | Double byte | 5MIN~20MIN | 8min |
| 2017 | 03/06/16 | Wire control parameter 7 External coil temp. to exit defrost mode | Double byte | 1℃~40℃ | 13℃ |
| 2018 | 03/06/16 | Wire control parameter 8 Ambient temperature setting value for extended defrosting cycle | Double byte | -30℃~5℃ | -10℃ |
| 2019 | 03/06/16 | Wire control parameter 9 Extended defrosting cycle | Double byte | 20MIN~90MIN | 45MIN |
| 2020 | 03/06/16 | Wire control parameter 10 Temp. difference between outdoor temp. and coil temp. to length defrost | Double byte | 0~30℃ | 10℃ |
| 2021 | 03/06/16 | Wire control parameter 11 Ambient temperature too low protection | Double byte | -41~0℃ | -35℃ |
| 2022 | 03/06/16 | Wire control parameter 12 Low ambient temperature protection parameters in cooling mode | Double byte | -1~20℃ | 5℃ |
| 2023 | 03/06/16 | Wire control parameter 13 Electronic expansion valve operation cycle | Double byte | 20S~90S | 30S |
| 2024 | 03/06/16 | Wire control parameter 14 Fix frequency target overheat degree setting | Double byte | -10℃~15℃ | 5℃ |
| 2025 | 03/06/16 | Wire control parameter 15 fix frequency expansion valve Manual and automatic selection | Double byte | 0-Manual\1-Auto | 1 |
| 2026 | 03/06/16 | Wire control parameter 16 Manual steps of fix frequency expansion valve | Double byte | 0~480 | 400 |
| 2027 | 03/06/16 | Wire control parameter 17 Maximum water temperature setting | Double byte | 20℃~90℃ | 55℃ |
| 2028 | 03/06/16 | Wire control parameter 18 Coolling minimum water temperature setting | Double byte | 3℃~15℃ | 12℃ |
| 2029 | 03/06/16 | Wire control parameter 19 Electric heating function selection | Double byte | 0 non，1 have | 1 |

| 2030 | 03/06/16 | Wire control parameter 20 Ambient temperature for turning on electric heater | Double byte | -41-45℃ | -20℃ |
| --- | --- | --- | --- | --- | --- |
| 2031 | 03/06/16 | Wire control parameter 21 Electric heating start delay | Double byte | 0-60MIN | 30min |
| 2032 | 03/06/16 | Wire control parameter 22 Current protection value of fix speed frequency compressor | Double byte | 0-50A | 15A |
| 2033 | 03/06/16 | Wire control parameter 23 Whether reduce the working frequency or not | Double byte | 0 off 1 on | 0 |
| 2034 | 03/06/16 | Wire control parameter 24 Target over heat of DC inverter main expansion valve | Double byte | -10℃~15℃ | 5℃ |
| 2035 | 03/06/16 | Wire control parameter 25 Centralized control scheme | Double byte | 0 Fast heating 1 Energy saving | 0 |
| 2036 | 03/06/16 | Wire control parameter 26 Module adjustment cycle | Double byte | 5~240 | 20 |
| 2037 | 03/06/16 | Wire control parameter 27 Forced open water pump emptying function | Double byte | 0 off 1 on | 0 |
| 2038 | 03/06/16 | Wire control parameter 28 Ambient temperature setting of low temperature forced water pump | Double byte | -25℃~5℃ | -10℃ |
| 2039 | 03/06/16 | Timing limit lock unit | Double byte | 0~99 | 0 |
| 2040 | 03/06/16 | Reserved | Double byte |  |  |
| 2041 | 03/06/16 | Reserved | Double byte |  |  |
| 2042 | 03/06/16 | Reserved | Double byte |  |  |
| 2043 | 03/06/16 | Reserved | Double byte |  |  |
| 2044 | 03/06/16 | Reserved | Double byte |  |  |
| 2045 | 03/06/16 | Reserved | Double byte |  |  |
| 2046 | 03/06/16 | Reserved | Double byte |  |  |
| 2047 | 03/06/16 | Reserved | Double byte |  |  |
| 2048 | 03/06/16 | Reserved | Double byte |  |  |
| 2049 | 03/06/16 | Reserved | Double byte |  |  |

| Address | Function | Content | Byte length | Function destiption | Remark |
| --- | --- | --- | --- | --- | --- |
| 2050 | 03 | Water inlet temperature | Double byte | -40℃~99℃ |  |
| 2051 | 03 | Water outlet temperature | Double byte | -40℃~99℃ |  |
| 2052 | 03 | Ambient temperature | Double byte | -40℃~99℃ |  |
| 2053 | 03 | System 1 DC inverter auxiliary circuit expansion valve opening | Double byte | 0~500 |  |
| 2054 | 03 | System 2 DC inverter auxiliary circuit expansion valve opening | Double byte | 0~500 |  |
| 2055 | 03 | System 1 inverter discharge temperature | Double byte | 0~150℃ |  |
| 2056 | 03 | System 1 inverter coil temperature | Double byte | -40℃~99℃ |  |
| 2057 | 03 | System 1 inverter suction temperature | Double byte | -40℃~99℃ |  |
| 2058 | 03 | System 1 inverter AC current input | Double byte | 0~99A |  |
| 2059 | 03 | System 1 inverter main circuit expansion valve opening | Double byte | Actual opening=this value*2 |  |
| 2060 | 03 | System 1 inverter cooling coil temperature | Double byte | -40℃~99℃ |  |
| 2061 | 03 | System 1 inverter bus voltage | Double byte | Actual value=this value *10 |  |
| 2062 | 03 | System 1 inverter IPM module temperature | Double byte |  |  |
| 2063 | 03 | System 1 inverter real power | Double byte |  |  |
| 2064 | 03 | System 1 inverter fan motor speed | Double byte |  |  |
| 2065 | 03 | System 1 inverter high pressure value | Double byte |  |  |
| 2066 | 03 | System 1 inverter low pressure value | Double byte |  |  |
| 2067 | 03 | System 1 inverter AC voltage input | Double byte |  |  |
| 2068 | 03 | System 1 inverter compressor actual running frequency | Double byte |  |  |
| 2069 | 03 | System 1 inverter EE high bit | Double byte |  |  |
| 2070 | 03 | System 1 inverter EE low bit | Double byte |  |  |
| 2071 | 03 | System 1 fixed frequency discharge temperature | Double byte | 0~150℃ |  |
| 2072 | 03 | System 1 fixed frequency coil temperature | Double byte | -40℃~99℃ |  |
| 2073 | 03 | System 1 fixed frequency suction | Double byte | -40℃~99℃ |  |
| 2074 | 03 | System 1 fixed frequency compressor current | Double byte | 0~99A |  |
| 2075 | 03 | System 1 fixed frequency main circuit expansion valve | Double byte | Actual value=this value *2 |  |

| 2076 | 03 | Fixed speed DC fan speed | Double byte |  |  |
| --- | --- | --- | --- | --- | --- |
| 2077 | 03 | Fixed speed AC voltage input voltage | Double byte |  |  |
| 2078 | 03 | Fixed frequency EE high bit | Double byte |  |  |
| 2079 | 03 | Fixed frequency EE low bit | Double byte |  |  |
| 2080 | 03 | System 2 inverter discharge temperature | Double byte | 0~150℃ |  |
| 2081 | 03 | System 2 inverter coil temperature | Double byte | -40℃~99℃ |  |
| 2082 | 03 | System 2 inverter suction temperature | Double byte | -40℃~99℃ |  |
| 2083 | 03 | System 2 inverter AC current input | Double byte | 0~99A |  |
| 2084 | 03 | System 2 inverter main circuit expansion valve opening | Double byte | Actual value=this value *2 |  |
| 2085 | 03 | System 2 inverter cooling coil temperature | Double byte | -40℃~99℃ |  |
| 2086 | 03 | System 2 inverter DC bus voltage | Double byte |  |  |
| 2087 | 03 | System 2 inverter IPM module temperature | Double byte |  |  |
| 2088 | 03 | System 2 inverter actual power | Double byte |  |  |
| 2089 | 03 | System 2 inverter fan motor speed | Double byte |  |  |
| 2090 | 03 | System 2 inverter inverter pressure value | Double byte |  |  |
| 2091 | 03 | System 2 inverter low pressure valve | Double byte |  |  |
| 2092 | 03 | System 2 inverter AC current input | Double byte |  |  |
| 2093 | 03 | System 2 inverter compressor actual running frequency | Double byte |  |  |
| 2094 | 03 | System 2 inverter EE high bit | Double byte |  |  |
| 2095 | 03 | System 2 inverter EE low bit | Double byte |  |  |
| 2096 | 03 | System 2 fixed frequency discharge temperature | Double byte | 0~150℃ |  |
| 2097 | 03 | System 2 fixed frequency coil temperature | Double byte | -40℃~99℃ |  |
| 2098 | 03 | System 2 fixed frequency suction temperature | Double byte | -40℃~99℃ |  |
| 2099 | 03 | System 2 fixed frequency compressor current | Double byte | 0~99A |  |
| 2100 | 03 | System 2 fixed frequency main circuit expansion valve | Double byte | Actual value=this value*2 |  |
| 2101 | 03 | Reserved | Double byte |  |  |
| 2102 | 03 | Reserved | Double byte |  |  |

| 2103 | 03 | Reserved | Double byte |  |  |
| --- | --- | --- | --- | --- | --- |
| 2104 | 03 | Reserved | Double byte |  |  |
| 2105 | 03 | Reserved | Double byte |  |  |
| 2106 | 03 | Reserved | Double byte |  |  |
| 2107 | 03 | Reserved | Double byte |  |  |
| 2108 | 03 | Reserved | Double byte |  |  |
| 2109 | 03 | Reserved | Double byte |  |  |
| 2110 | 03 | System status | Double byte |  |  |
| 2111 | 03 | Fixed speed system error error symbol | Double byte |  |  |
| 2112 | 03 | System 1 inverter error symbol | Double byte |  |  |
| 2113 | 03 | System 2 inverter error symbol | Double byte |  |  |
| 2114~2115 | 03 | Fixed frequency system protection symbol | Four bytes |  |  |
| 2116 | 03 | System 1 inverter protection symbol | Double byte |  |  |
| 2117 | 03 | System 2 inverter protection symbol | Double byte |  |  |
| 2118 | 03 | System switch status | Double byte |  |  |
| 2119 | 03 | Reserved | Double byte |  |  |
| 2120 | 03 | Reserved | Double byte |  |  |

| 2110 | BIT0: Wire control switch status |  |
| --- | --- | --- |
| System status | BIT1: Compressor 1 status |  |
|  | BIT2: Compressor 2 status |  |
|  | BIT3: High speed wind (any one of bit3, bit4 and bit5 is 1, which means fan starts) |  |
|  | BIT4: Medium speed wind (any one of bit3, bit4 and bit5 is 1, which means the fan starts) |  |
|  | BIT5: Low speed wind (any one of bit3, bit4 and bit5 is 1, which means the fan starts) |  |
|  | BIT6: circulating water pump |  |
|  | BIT7: Status of four-way valve 1 BIT8: Status of four-way valve 2 BIT9: Crankshaft heating 1 status BIT10: Crankshaft heating 2 status BIT11: Electric heating state BIT12: Chassis heating BIT13~BIT15: Reserved |  |
|  | BIT8: Status of four-way valve 2 |  |
|  | BIT9: Crankshaft heating 1 status |  |
|  | BIT10: Crankshaft heating 2 status |  |
|  | BIT11: Electric heating state BIT12: Chassis heating BIT13~BIT15: Reserved |  |
|  | BIT12: Chassis heating |  |
|  | BIT13~BIT15: Reserved |  |
| 2111 | BIT0: System 1 fixed frequency discharge error E02 | harge error |
|  | BIT1: System 2 fixed frequency discharge error E04 |  |
| Fixed speed system error symbol | BIT2: System 1 fixed frequency coil error E06 |  |
|  | BIT3: System 2 fixed frequency coil error E08 |  |
|  | BIT4: System 1 fixed frequency suction error E10 |  |
|  | BIT5: System 1 fixed frequency suction error E12 |  |
|  | BIT6: Communication failure between fixed frequency board and inverter board 1 board 1 | a |
|  | 1 E39 BIT7: Communication failure between fixed frequency and and inverter board 2 E E40 | E40 |

|  | BIT8: Fixed frequency system EE error E28 BIT9: Fixed frequency inverter fan error FA BIT10: Water inlet temperature sensor error E19 BIT11:Water outlet temperature sensor error E18 BIT12:Ambient temperature sensor error E22 BIT13Communication failure with remote control E21 BIT14: Time limited locking unit E23 BIT15:Reserved |
| --- | --- |
| 2112 | BIT0: Frequency conversion exhaust fault of system 1 E01 |
|  | BIT1: System 1 frequency conversion external coil failure E05 |
| System 1 inverter error | BIT2: Frequency conversion air return fault of system 1 E09 |
|  | BIT3: System 1 frequency conversion internal coil failure E13 |
|  | BIT4: Reserved |
|  | BIT5: Communication fault between inverter main board 1 and driver board E41 |
|  | BIT6: Frequency conversion main board 1EE fault E43 BIT7: Inverter drive 1 IPM module failure R13 BIT8: Variable frequency drive 1 compressor starts abnormally (phase loss, reverse rotation) R02 BIT9: Frequency conversion drive 1EE fault E43 BIT10~BIT15: Reserved |
|  | BIT7: Inverter drive 1 IPM module failure R13 |
|  | BIT8: Variable frequency drive 1 compressor starts abnormally (phase loss, reverse rotation) R02 |
|  | BIT9: Frequency conversion drive 1EE fault E43 |
|  | BIT10~BIT15: Reserved |
| 2113 | BIT0: Frequency conversion exhaust fault of system 2 E03 |
| System 2 inverter error | BIT1: System 2 frequency conversion external coil failure E07 |
| error | BIT2: system 2 frequency conversion air return fault E11 |
|  | BIT3: system 2 frequency conversion internal coil failure E15 |
|  | BIT4: Reserved |
|  | BIT5: Communication fault between inverter main board 2 and driver board E42 |
|  | BIT6: Frequency conversion main board 2EE fault E44 |
|  | BIT7: Inverter drive 2IPM module fault R30 |
|  | BIT8: Abnormal startup of variable frequency drive 2 compressor (phase loss, reverse rotation) R26 |
|  | BIT9: Frequency conversion drive 2EE fault E44 |
|  | BIT10~BIT15: Reserved |
| 2114~2115 | BIT0: water flow switch protection P01 |
| Fixed frequency system protection | BIT1: fixed frequency plate phase sequence protection P10 |
|  | BIT2: System 1 constant frequency high-voltage switch protection P03 |
|  | BIT3: System 2 constant frequency high-voltage switch protection P05 |
|  | BIT4: System 1 constant frequency low-voltage switch protection P07 |
|  | BIT5: Fixed frequency low-voltage switch protection of system 2 P09 |
|  | BIT6: System 1 constant frequency exhaust over temperature protection P12 |
|  | BIT7: System 2 constant frequency exhaust over temperature protection P14 |
|  | BIT8: Protection against excessive inlet and outlet water temperature difference P15difference P15 |
|  | Different P15 BIT9:制冷过冷保护 P16 |
|  | BIT10: First stage antifreeze protection P17 BIT11: Second stage antifreeze protection P17 |
|  | BIT12: Electric heating overheat protection P18 BIT13: System 1 constant frequency AC current protection BIT14: Constant frequency AC current protection of system 2 BIT15: Fan overload protection BIT16: Low ambient temperature protection (i.e. 2015bit0) BIT17~BIT31: P20P22P24PC reserved |

| 2116 | BIT0: system 1 inverter high pressure switch protection P02 |  |  |  |
| --- | --- | --- | --- | --- |
| System 1 inverter protection | BIT1: system 1 inverter low pressure switch protection P06 BIT2: System 1 inverter exhaust temperature too high protection P11 |  |  |  |  |
|  | BIT3: system 1 inverter AC current protection P19 |  |  |  |
|  | BIT4: system 1 inverter cooling outdoor coil overheating protection P31 |  |  |  |
|  | BIT5: system 1 inverter cooling indoor coil overheating protection P33 |  |  |  |
|  | BIT6: Inverter drive 1IPM over temperature protection R01 |  |  |  |
|  | BIT7: system 1 inverter compressor current protection R06 |  |  |  |
|  | BIT8: System 1 inverter AC voltage protection R10 |  |  |  |
|  | BIT9: system 1inverter bus voltage protection R11 |  |  |  |
|  | BIT10: shell top protection of system 1 variable frequency compressor |  |  |  |
|  | R20 |  |  |  |
|  | BIT11~BIT15: Reserved |  |  |  |
| 2117 | BIT0: system2 inverter high pressure switch protection P04 |  |  |  |
| System 2 inverter protection | BIT1: system 2 inverter low pressure switch protection P08 BIT2: System 2 inverter exhaust temperature too high protection P13 BIT2: System 1 inverter exhaust temperature too high protection P11 |  |  |  |
|  | BIT3: system 2 inverter AC current protection P21 |  |  |  |
|  | BIT4: system 2 inverter cooling outdoor coil overheating protection P32 |  |  |  |
|  | BIT5: system 2 inverter cooling indoor coil overheating protection P34 |  |  |  |
|  | BIT6: Inverter drive 2 IPM over temperature protection R25 |  |  |  |
|  | BIT7: system 2 inverter compressor current protection R27 |  |  |  |
|  | BIT8: System 2 inverter AC voltage protection R28 |  |  |  |
|  | BIT9: system 2inverter bus voltage protection R29 |  |  |  |
|  | BIT10: shell top protection of system2 variable frequency compressor |  |  |  |
|  | R31 |  |  |  |
|  | BIT11~BIT15: Reserved |  |  |  |
| 2118 | BIT0: System 1 fixed frequency high pressure switch |  |  |  |
| System switch status | BIT1: System 1 fixed frequency low pressure switch |  |  |  |
|  | BIT2: System 2 fixed frequency high pressure switch |  |  |  |
|  | BIT3: System 2 fixed frequency low pressure switch |  |  |  |
|  | BIT4: AC online switch |  |  |  |
|  | BIT5: Water flow switch BIT6: Emergency switch |  |  |  |
|  | BIT6: Emergency switch |  |  |  |
|  | BIT7: Electric heating overheat protection switch |  |  |  |
|  | BIT8~BIT14: Reserved |  |  |  |